## Methodology
Steps to Calculate Fugitive Emissions Required Ventilation due to Fugitive Emissions
1. Find Building Information and populate all deminsions
2. Set contingency factor based on how confident you feel with current P&ID Rev.
3. Using the P&IDs count and catorgrize all items were fugitives emsiions may leak from
4. Select the appropriate facility type
5. Populate gas stream information.
Formula's Used in Calculations
Corrected Volume [ft3/lb-mol] = V
V = (Vconst x Ta) / Tconst |  |  | Where: | Vconst = 359 [ft3]
Ta = Ambient Building Temperature in Rankine
Tconst = 492 [R]
Total Hydrocarbon leak Rate [cfm] = G
G = [( E) (V)] / [60 x mwavg] |  |  | Where: | E = Emission Rate [lb/hr]
V = Corrected Volume [ft3/lb-mol]
mwavg = Average Molecular Weight
Fresh Air Introduction Rate [cfm] = Qr
Qr = G/C |  |  | Where: | G = Total Hydrocarbon Leak Rate [cfm]
C = LEL x 5% concentration
Minimum Fresh Air Introduction Rate [cfm] = Q
Q = Qr x 4 |  |  | Where: | Qr = Fresh Air Quality Rate [cfm]
4 = Safety Factor (API RP-505 para. )
Minimum Air Change Required Per Hour
= (Q x 60) /Bldg. Vol.
Steps to Calculate the Buildings Natural Ventilation
1. Measure the distance from the center of the lower and upper building vents
2. Determine the number and size of vents on building
3. Determine what case you would like to study to set louver opening percent (i.e. 100% open for summer season)
Formula's Used in Calculations
Neutral Pressure Level [m] = h
h= | H | (Assume Ti > To) | Where: | h = Neutral Pressure Level above center of lower vent [m]
| 1 + [(A1/A2)2(Ti/To)] |  |  | A1 = Free area of lower vent [m2]
A2 = Free area of upper vent [m2]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
H = Vertical distance (center-t-center) between A1 and A2 [m]
Air Flow due to Stack Effect [m3/hr] = Q
Q = [15940 (Cv)(A) [h (Ti - To) / Ti]1/2 ] x 2 |  |  | Where: | 15940 = Conversion Factor
Cv = Effectiveness of Openings (Percent open values)
If A1 and A2 are not equal, Q is multiplyed but corrention |  |  |  | A = Area of the smallest of the lower and upeer vents [m2]
factor from API RP-500 Figure 1. |  |  |  | h = Neutral Pressure Level [m]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
2 = Safety Factor (API RP-500 para. 6.3.2.4.5)
Air Changes Per Hour due to Stack Effect
= (Q x 60) /Bldg. Vol.
References
[1] | API RP-505
[2] | API RP-500
[3] | ASHRAE Handbook, Chapter 22

## Fugitive Emissions
|  |  |  | Spreadsheet: |  | Fugitive Emissions Study
Document Number:
|  |  |  | Client: |  | ABC Engineering
|  |  |  | Project Name: |  | Blackswan c-46-C
|  |  |  | Project Number: |  | 2016-425
|  |  |  | Building: |  | Sour Gas Dehy. Skid (BU-406)
|  |  |  | Date: |  | 2018-10-29
|  |  |  | P&ID: |  | ABC 16332-PID-00-01-14 to 151
|  |  |  | Building Drawing: |  | Alco Dwg D-2017-8876-50A-001/004
Spreadsheet Description: |  | Calculates the amount (lbs) of flammable gas and vapour emitted during normal operation of an oil and gas facility building. Utilized to determine area classification.
Rev | Description |  |  |  | Date | By | Checked | Approved
A | Issued for Review |  |  |  | 2017-09-29 | RWS | TA
0 | Issued for Implementation |  |  |  | 2019-03-19 | RWS | TA | TA
Building Parameters
Description
Maximum Ambient Temperature |  |  | 30 | C | 86 | F | 546 | R
Length |  |  | 11.6 | m
Width |  |  | 4.4 | m
Cavity Length |  |  | 0 | m
Cavity Width |  |  | 0 | m
Length of Vessel |  |  | 0 | m
Radius of Vessel |  |  | 0 | m
Height to Eave |  |  | 3.042 | m
Height from Eave to Peak |  |  | 0.83 | m
Base Area |  |  | 51.04 | m2
Volume from Eave to Peak |  |  | 21.1816 | m3
Volume up to Eave |  |  | 155.2637 | m3
Volume of Vessel |  |  | 0 | m3
Total Volume |  |  | 176.4453 | m3
Bldg volume that contains equipment |  |  | 20 | %
Building Volume Without Equipment |  |  | 141.1562 | cu-m | 4984.8897 | cu-ft
Max % of Lower Explosive Limit (LEL) |  |  | 25 | %
Contingency Factor (CF) |  |  | 15 | %
[9 empty] | P&ID Name: |  |  | 16332-PID-00-01
Number of Items Per Substance | [8 empty] | 146 |  |  | 147 |  |  | 148 |  |  | 149 |  |  | 150 |  |  | 151 |  |  | P&ID Page |  |  | P&ID Page |  |  | P&ID Page |  |  | P&ID Page
Items |  |  | Acid Gas | Condensate | Fuel Gas | Total |  |  | AG | Cond | FG | AG | Cond | FG | AG | Cond | FG | AG | Cond | FG | AG | Cond | FG | AG | Cond | FG | Sub1 | Sub2 | Sub3 | Sub1 | Sub2 | Sub3 | Sub1 | Sub2 | Sub3 | Sub1 | Sub2 | Sub3
Connections |  |  | 70 | 14 | 16 | 100 | . |  | 14 | 14 | 8 | 26 |  | 8 | [9 empty] | 30
Flanges |  |  | 72 | 28 | 1 | 101 | . |  | 31 | 28 | 0 | 13 |  | 1 | [9 empty] | 28
Open-Endeds |  |  | 13 | 3 | 1 | 17 | . |  | 3 | 3 | 0 | 0 |  | 1 | [9 empty] | 10
Pumps |  |  | 0 | 0 | 0 | 0 | . |  | 0 | 0 | 0 | 0 |  | 0 | [9 empty] | 0
Valves |  |  | 86 | 27 | 17 | 130 | . |  | 24 | 27 | 4 | 23 |  | 13 | [9 empty] | 39
*Others |  |  | 22 | 12 | 2 | 36 | . |  | 8 | 12 | 1 | 5 |  | 1 | [9 empty] | 9
Fugitive Emissions Calculation Summary
Facility Type |  |  | Item |  | QTY | Prediction Factor (lbs/day) |  | Total Emissions (lbs/day)
|  |  | Connections |  | 0 | 0.00866 |  | 0 |  |  | 4
|  |  | Flanges |  | 0 | 0.00407 |  | 0
|  |  | Open-endeds |  | 0 | 0.0638 |  | 0
|  |  | Pumps |  | 0 | 0.0168 |  | 0
|  |  | Valves |  | 0 | 0.07 |  | 0
|  |  | *Others |  | 0 | 0.397 |  | 0
[7 empty] | Subtotal: | 0
|  |  | Connections |  | 0 | 0.000422 |  | 0
|  |  | Flanges |  | 0 | 0.00116 |  | 0
|  |  | Open-endeds |  | 0 | 0.00818 |  | 0
|  |  | Pumps |  | 0 | 0.0168 |  | 0
|  |  | Valves |  | 0 | 0.000686 |  | 0
|  |  | *Others |  | 0 | 0.0037 |  | 0
[7 empty] | Subtotal: | 0
|  |  | Connections |  | 0 | 0.017 |  | 0
|  |  | Flanges |  | 0 | 0.00623 |  | 0
|  |  | Open-endeds |  | 0 | 0.0363 |  | 0
|  |  | Pumps |  | 0 | 0.0103 |  | 0
|  |  | Valves |  | 0 | 0.139 |  | 0
|  |  | *Others |  | 0 | 0.486 |  | 0
[7 empty] | Subtotal: | 0
|  |  | Connections |  | 100 | 0.0145 |  | 1.45
|  |  | Flanges |  | 101 | 0.0232 |  | 2.3432
|  |  | Open-endeds |  | 17 | 0.0546 |  | 0.9282
|  |  | Pumps |  | 0 | 0.609 |  | 0
|  |  | Valves |  | 130 | 0.204 |  | 26.52
|  |  | *Others |  | 36 | 0.257 |  | 9.252
[7 empty] | Subtotal: | 40.4934
|  |  | Connections |  | 0 | 0.0057 |  | 0
|  |  | Flanges |  | 0 | 0.0104 |  | 0
|  |  | Open-endeds |  | 0 | 0.0537 |  | 0
|  |  | Pumps |  | 0 | 0.0103 |  | 0
|  |  | Valves |  | 0 | 0.0272 |  | 0
|  |  | *Others |  | 0 | 0.367 |  | 0
[7 empty] | Subtotal: | 0
[5 empty] | Total = |  | 40.4934 | lbs/day
[5 empty] | = |  | 1.6872 | lbs/hr
[5 empty] | Total w/CF = |  | 46.5674 | lbs/day
[5 empty] | = |  | 1.9403 | lbs/hr
Adequate Ventilation Rate Calculation: |  |  |  | Sour Gas Dehy. Skid (BU-406)
Hydrocarbon |  |  | C1 | C2 - C4 | Field Gas | C5 + | C6 +
Average Molecular Weight |  |  | 16.04 | 44.1 | 26.12 | 72.15 | 86.18
Substance |  |  | Acid Gas |  | Condensate |  | Fuel Gas
Lower Flammable Limit |  |  | 4% |  | 1.5% |  | 5%
Molecular Weight (g/mol) |  |  | 34.1 |  | 81.6 |  | 16.04
Items | Connections |  | 70/100 |  | 14/100 |  | 16/100
| Flanges |  | 72/101 |  | 28/101 |  | 1/101
| Open-Endeds |  | 13/17 |  | 3/17 |  | 1/17
| Pumps |  | 0/0 |  | 0/0 |  | 0/0
| Valves |  | 86/130 |  | 27/130 |  | 17/130
| *Others |  | 22/36 |  | 12/36 |  | 2/36
Hydrocarbon |  |  | H2S |  | >=C5 |  | 87% C1
Items | Connections |  | 0.7 |  | 0.14 |  | 0.16
| Flanges |  | 0.71287 |  | 0.27723 |  | 0.009901
| Open-Endeds |  | 0.76471 |  | 0.17647 |  | 0.058824
| Pumps |  | 0 |  | 0 |  | 0
| Valves |  | 0.66154 |  | 0.20769 |  | 0.13077
| *Others |  | 0.61111 |  | 0.33333 |  | 0.055556
% Emissions |  |  | 65.67% |  | 23.73% |  | 10.6%
Calculated Hydrocarbon Molecular Weight (g/mol) |  |  | 43.4568
Combined LFL of Mixture |  |  | 2.911%
Corrected Volume (V) |  |  | 398.4024 | ft3/lb-mol
Total Hydrocarbon Leak Rate (G) |  |  | 0.29647 | cfm
Fresh Air Introduction Rate (Qr) |  |  | 40.7434 | cfm
Min. Fresh Air Introduction Rate (Q) |  |  | 162.9736 | cfm
Min. Air Change Required for Adequate Ventilation |  |  | 1.9616 | Air Changes Per Hour
*Others includes: instruments, loading arms, pressure relief valves, stuffing boxes, compressor seals,
dump lever arms, vents
References
[1] | API RP-505
[2] | API PUBL No. 4615

## Natural Ventilation
|  |  |  | Spreadsheet: |  | Natural Ventilation Calculation
Document Number:
|  |  |  | Client: |  | ABC Engineering
|  |  |  | Project Name: |  | Blackswan c-46-C
|  |  |  | Project Number: |  | 2016-425
|  |  |  | Building: |  | Sour Gas Dehy. Skid (BU-406)
*complete Fugitive Emissions worksheet prior |  |  |  | Date: |  | 2018-10-29
to filling out this spreadsheet |  |  |  | P&ID: |  | ABC 16332-PID-00-01-14 to 151
**data in DARK RED is copied from the Fugitive emissions worksheet |  |  |  | Building Drawing: |  | Alco Dwg D-2017-8876-50A-001/004
|  |  |  | Case: |  | Summer - Louvres 100% Open
Spreadsheet Description: |  | For naturally ventilated enclosed areas. Air flow due to stack effect (thermal forces) provides adequate ventilation if the inlen and oulet vent openings are properly sized and located (recommended for areas under 1000 cu-ft)
Rev | Description |  |  |  | Date | By | Checked | Approved
A | Issued for Review |  |  |  | 2017-09-29 | RWS | TA
0 | Issued for Implementation |  |  |  | 2019-03-19 | RWS | TA | TA
Building Parameters
Description
Outdoor Air Temperature |  |  | 20 | C | 68 | F | 293.15 | K
Indoor Air Temperature |  |  | 32 | C | 89.6 | F | 305.15 | K
Length |  |  | 11.6 | m | 38.0596 | ft
Width |  |  | 4.4 | m | 14.4364 | ft
Eave Height |  |  | 3.042 | m | 9.9808 | ft
Eave to Peak Height |  |  | 0.83 | m | 2.7232 | ft
Volume |  |  | 141.1562 | cu-m | 4984.8897 | cu-ft
Vertical Distance Between Upper and Lower Vent Openings (center-to-center) |  |  | 2.73 | m | 8.9571 | ft
Vent Openings |  |  | Length OR # Circular |  | Width OR Diameter |  | Area
Lower | Rectangular Vents |  | 0.406 | 1.3321 | 0.406 | 1.3321 | 0.16484 | 1.7745
Upper | Rectangular Vents |  | 0.3 | 0.9843 | 0.3 | 0.9843 | 0.09 | 0.96885
| Circular Vents |  | 0 | 0 | 1 | 3.281 | 0 | 0
Number of Vents |  |  | .
| Lower |  | 4
| Upper Rectangular |  | 2
Open Area |  |  | .
| A1 |  | 0.16484
| A2 |  | 0.18
% Open |  |  | .
| Lower Vents |  | 25%
| Upper Vents |  | 100%
Effectiveness of Openings |  |  | 100%
Stack Effect Calculation
Description |  |  | Lower/Upper (A1/A2) |  | Upper/Lower (A2/A1)
Vent Opening Ratios |  |  | 0.91576 |  | 1.092 |  | .
Neutral Pressure Level |  |  | 1.4576 |  | . | . | .
Natural Ventilation Due to Stack
Both openings as smallest |  |  | 2.2283 | Air Changes Per Hour
One opening larger than the other |  |  | 2.4099 | Air Changes Per Hour
|  |  | . | . | . | . | .
References
[1] | API RP-505

## API RP-505 Figure 1
Ratio of
Outlet to | Increase
Inlet Area | (%)
1 | 0
1.01 | 2.5
1.02 | 5
1.035 | 6.15
1.05 | 7.3
1.075 | 8.15
1.1 | 9
1.125 | 10
1.15 | 11
1.175 | 12
1.2 | 13
1.225 | 13.6
1.25 | 14.2
1.275 | 14.85
1.3 | 15.5
1.325 | 16.05
1.35 | 16.6
1.375 | 17.2
1.4 | 17.8
1.425 | 18.15
1.45 | 18.5
1.475 | 18.8
1.5 | 19.1
1.525 | 19.55
1.55 | 20
1.575 | 20.5
1.6 | 21
1.625 | 21.4
1.65 | 21.8
1.675 | 22.15
1.7 | 22.5
1.725 | 22.9
1.75 | 23.3
1.775 | 23.65
1.8 | 24
1.85 | 24.5
1.9 | 25
1.95 | 25.6
2 | 26.2
2.05 | 26.8
2.1 | 27.4
2.15 | 27.8
2.2 | 28.2
2.25 | 28.7
2.3 | 29.2
2.35 | 29.6
2.4 | 30
2.45 | 30.4
2.5 | 30.8
2.55 | 31.1
2.6 | 31.4
2.65 | 31.7
2.7 | 32
2.75 | 32.35
2.8 | 32.7
2.9 | 33.25
3 | 33.8
3.125 | 34.4
3.25 | 35
3.325 | 35.35
3.4 | 35.7
3.45 | 35.95
3.5 | 36.2
3.6 | 36.5
3.7 | 36.8
3.85 | 37.15
4 | 37.5
4.25 | 37.9
4.5 | 38.3
4.75 | 38.5
5 | 38.7
5.25 | 38.85
5.5 | 39
5.6 | 39
5.7 | 39
5.8 | 39
6 | 39
7 | 39
8 | 39
9 | 39
10 | 39

## Calculation Sheet Revisions
Revision Log:
Rev | Description |  | Date | By | Checked | Approved
0 | Standardizing Formatting of Spreadsheet |  | 2015-07-23 | RW
1 | Added multiple P&IDs for counting |  | Oct 2 2017 | WDS

## Backworkings (hidden)
Round
Rectangular | [8 empty] | (York Demister Method)
(GPSA Method)
(Manual Method)
Low Liquid Level Height
Edmonton Exchanger Standard Sizes (inches) | Standard Thicknesses (in) | Temp (C) | Temp (F) | Allowable Stress (ksi) |  | Vessel Diameter | Vertical LLL
162 | 1.5 | 65.5556 | 150 | 20 |  |  | <300 psia | > 300 psia
156 | 1.375 | 93.3333 | 200 | 20 |  | in. | in. | in.
150 | 1.25 | 121.1111 | 250 | 20 |  | 0 | 15 | 6
144 | 1.125 | 148.8889 | 300 | 20 | <= | 48 | 15 | 6
138 | 1 | 204.4444 | 400 | 19.9 |  | 72 | 15 | 6
132 | 0.875 | 260 | 500 | 19 |  | 96 | 15 | 6
126 | 0.75 | 315.5556 | 600 | 17.9 |  | 120 | 6 | 6
120 | 0.625 | 343.3333 | 650 | 17.3 |  | 144 | 6 | 6
114 | 0.5 | 371.1111 | 700 | 16.8 |  | 192 | 6 | 6
108 | 0.375
102 | 0.25
96
90
84
72
66
60
54
48
42
36
34
32
30
28
26
24
20