## Methodology
Steps to Calculate Fugitive Emissions Required Ventilation due to Fugitive Emissions
1. Find Building Information and populate all deminsions
2. Set contingency factor based on how confident you feel with current P&ID Rev.
3. Using the P&IDs count and catorgrize all items were fugitives emsiions may leak from
4. Select the appropriate facility type
5. Populate gas stream information.
Formula's Used in Calculations
Corrected Volume [ft3/lb-mol] = V
V = (Vconst x Ta) / Tconst |  |  | Where: |  | Vconst = 359 [ft3]
Ta = Ambient Building Temperature in Rankine
Tconst = 492 [R]
Total Hydrocarbon leak Rate [cfm] = G
G = [( E) (V)] / [60 x mwavg] |  |  | Where: | E = Emission Rate [lb/hr]
V = Corrected Volume [ft3/lb-mol]
mwavg = Average Molecular Weight
Fresh Air Introduction Rate [cfm] = Qr
Qr = G/C |  |  | Where: |  | G = Total Hydrocarbon Leak Rate [cfm]
C = LEL x 5% concentration
Minimum Fresh Air Introduction Rate [cfm] = Q
Q = Qr x 4 |  |  | Where: |  | Qr = Fresh Air Quality Rate [cfm]
4 = Safety Factor (API RP-505 para. )
Minimum Air Change Required Per Hour
= (Q x 60) / Bldg. Vol.
Steps to Calculate the Buildings Natural Ventilation
1. Measure the distance from the center of the lower and upper building vents
2. Determine the number and size of vents on building
3. Determine what case you would like to study to set louver opening percent (i.e. 100% open for summer season)
Formula's Used in Calculations
Neutral Pressure Level [m] = h
h= | H | (Assume Ti > To) |  | Where: | h = Neutral Pressure Level above center of lower vent [m]
| 1 + [(A1/A2)2(Ti/To)] |  | A1 = Free area of lower vent [m2]
A2 = Free area of upper vent [m2]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
H = Vertical distance (center-t-center) between A1 and A2 [m]
Air Flow due to Stack Effect [m3/hr] = Q
Q = [15940 (Cv)(A) [h (Ti - To) / Ti]1/2 ] x 2 |  |  | Where: | 15940 = Conversion Factor
Cv = Effectiveness of Openings (Percent open values)
If A1 and A2 are not equal, Q is multiplyed but corrention |  |  |  |  | A = Area of the smallest of the lower and upeer vents [m2]
factor from API RP-500 Figure 1. |  |  |  |  | h = Neutral Pressure Level [m]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
2 = Safety Factor (API RP-500 para. 6.3.2.4.5)
Air Changes Per Hour due to Stack Effect
= (Q x 60) /Bldg. Vol.
References
[1] | API RP-505
[2] | API RP-500
[3] | ASHRAE Handbook, Chapter 22

## Fugitive Emission
|  |  |  | Spreadsheet: |  | Fugitive Emissions Study
Document Number:
|  |  |  | Client: |  | Client Name
|  |  |  | Project Name: |  | Project Name
|  |  |  | Project Number: |  | Project Number
|  |  |  | Building: |  | Ranger station
|  |  |  | Date: |  | 2020-11-25
|  |  |  | P&ID: |  | ABC 16332-PID-00-01-14 to 151
|  |  |  | Building Drawing: |  | TODO - get S3 Link
Spreadsheet Description: |  | Calculates the amount (lbs) of flammable gas and vapour emitted during normal operation of an oil and gas facility building. Utilized to determine area classification.
Rev | Description |  |  |  | Date | By | Checked | Approved
A | Issued for review |  |  |  | 29-Sep-17 | RWS | TA
B | Issued for review |  |  |  | 8-March-21 | RWS | TA
C | Issued for review |  |  |  | 29-Sep-17 | RWS | TA
Building Parameters
Description
Maximum Ambient Temperature |  |  | 25 | C | 77 | F | 536.67 | R
Length |  |  | 10 | m
Width |  |  | 10 | m
Cavity Length |  |  | 4 | m
Cavity Width |  |  | 4 | m
Length of Vessel |  |  | 5 | m
Radius of Vessel |  |  | 5 | m
Height to Eave |  |  | 15 | m
Height from Eave to Peak |  |  | 20 | m
Base Area |  |  | 84 | m2
Volume from Eave to Peak |  |  | 840 | m3
Volume up to Eave |  |  | 1260 | m3
Volume of Vessel |  |  | 78.5398 | m3
Total Volume |  |  | 2021.4602 | m3
Bldg volume that contains equipment |  |  | 25 | %
Building Volume Without Equipment |  |  | 1516.0951 | cu-m | 53540.8998 | cu-ft
Max % of Lower Explosive Limit (LEL) |  |  | 18 | %
Contingency Factor (CF) |  |  | 25 | %
Number of Items Per Substance | [19 empty] | P&ID Name: | 1211104-M-PID-01-002_4400x6800.jpg | [14 empty] | P&ID Name: | 1211104-M-PID-01-031.jpg | [14 empty] | P&ID Name: | 1211104-M-PID-01-002_4400x6800.jpg | [14 empty] | P&ID Name: | 1211104-M-PID-01-031.jpg
Items |  |  | Diluent | Fuel gas | Hydrocarbon Liquid | Hydrocarbon Vapour | Hot Oil | Instrumentgas | Uquifiedpetroleum Gas | Produced Emulsion | Produced gas | Sales Gas | Slop Oil | Sales Oil | Acid Gas | Highpressure Flare | Low Pressure_Flare | Methanol | Totals | Diluent | Fuel gas | Hydrocarbon Liquid | Hydrocarbon Vapour | Hot Oil | Instrumentgas | Uquifiedpetroleum Gas | Produced Emulsion | Produced gas | Sales Gas | Slop Oil | Sales Oil | Acid Gas | Highpressure Flare | Low Pressure_Flare | Methanol | Diluent | Fuel gas | Hydrocarbon Liquid | Hydrocarbon Vapour | Hot Oil | Instrumentgas | Uquifiedpetroleum Gas | Produced Emulsion | Produced gas | Sales Gas | Slop Oil | Sales Oil | Acid Gas | Highpressure Flare | Low Pressure_Flare | Methanol | Diluent | Fuel gas | Hydrocarbon Liquid | Hydrocarbon Vapour | Hot Oil | Instrumentgas | Uquifiedpetroleum Gas | Produced Emulsion | Produced gas | Sales Gas | Slop Oil | Sales Oil | Acid Gas | Highpressure Flare | Low Pressure_Flare | Methanol | Diluent | Fuel gas | Hydrocarbon Liquid | Hydrocarbon Vapour | Hot Oil | Instrumentgas | Uquifiedpetroleum Gas | Produced Emulsion | Produced gas | Sales Gas | Slop Oil | Sales Oil | Acid Gas | Highpressure Flare | Low Pressure_Flare | Methanol
Connections |  |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 106 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flanges |  |  | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 98 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open Endeds |  |  | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 62 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Valves |  |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 125 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 29 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 29 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Others |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fugitive Emissions Calculation Summary
Facility Type |  |  | Item |  | QTY | Prediction Factor (lbs/day) |  | Total Emissions (lbs/day)
Light Crude |  |  | connections |  | 139 | 0.00866 |  | 1.2037
Light Crude |  |  | flanges |  | 136 | 0.00407 |  | 0.55352
Light Crude |  |  | open-endeds |  | 82 | 0.0638 |  | 5.2316
Light Crude |  |  | pumps |  | 0 | 0.0168 |  | 0
Light Crude |  |  | valves |  | 166 | 0.07 |  | 11.62
Light Crude |  |  | others |  | 19 | 0.397 |  | 7.543
[5 empty] | Total = |  | 26.1519 | lbs/day
[5 empty] | = |  | 1.0897 | lbs/hr
[5 empty] | Total w/CF = |  | 30.8592 | lbs/day
[5 empty] | = |  | 1.2858 | lbs/hr
Adequate Ventilation Rate Calculation
Hydrocarbon |  |  | C1 | C2 - C4 | Field Gas | C5 + | C6 +
Average Molecular Weight |  |  | 16.04 | 44.1 | 26.12 | 72.15 | 86.18
Substance |  |  | acid gas |  | condensate |  | fuel gas
Lower Flammable Limit |  |  | 4.0 |  | 1.5 |  | 5.0
Molecular Weight (g/mol) |  |  | 34.1 |  | 81.6 |  | 16.04
Items | Connection |  | 0/139 | 18/139 | 0/139 | 0/139 | 0/139 | 0/139 | 0/139 | 106/139 | 15/139 | 0/139 | 0/139 | 0/139 | 0/139 | 0/139 | 0/139 | 0/139
| Flanges |  | 0/136 | 11/136 | 0/136 | 0/136 | 0/136 | 0/136 | 0/136 | 98/136 | 27/136 | 0/136 | 0/136 | 0/136 | 0/136 | 0/136 | 0/136 | 0/136
| Open Endeds |  | 0/82 | 8/82 | 0/82 | 0/82 | 0/82 | 0/82 | 0/82 | 62/82 | 12/82 | 0/82 | 0/82 | 0/82 | 0/82 | 0/82 | 0/82 | 0/82
| Pumps |  | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0 | 0/0
| Valves |  | 0/166 | 18/166 | 0/166 | 0/166 | 0/166 | 0/166 | 0/166 | 125/166 | 23/166 | 0/166 | 0/166 | 0/166 | 0/166 | 0/166 | 0/166 | 0/166
| Others |  | 0/19 | 1/19 | 0/19 | 0/19 | 0/19 | 0/19 | 0/19 | 17/19 | 1/19 | 0/19 | 0/19 | 0/19 | 0/19 | 0/19 | 0/19 | 0/19
Items | Connection |  | 0 | 0.1295 | 0 | 0 | 0 | 0 | 0 | 0.76259 | 0.10791 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Flanges |  | 0 | 0.080882 | 0 | 0 | 0 | 0 | 0 | 0.72059 | 0.19853 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Open Endeds |  | 0 | 0.097561 | 0 | 0 | 0 | 0 | 0 | 0.7561 | 0.14634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Valves |  | 0 | 0.10843 | 0 | 0 | 0 | 0 | 0 | 0.75301 | 0.13855 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Others |  | 0 | 0.052632 | 0 | 0 | 0 | 0 | 0 | 0.89474 | 0.052632 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% Emissions |  |  | 0.09055 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79426 | 0.11519 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculated Hydrocarbon Molecular Weight (g/mol) |  |  | 1
Combined LFL of Mixture |  |  | 1
Corrected Volume (V) |  |  | 391.5946 | ft3/lb-mol
Total Hydrocarbon Leak Rate (G) |  |  | 8.3919 | cfm
Fresh Air Introduction Rate (Qr) |  |  | 46.6215 | cfm
Min. Fresh Air Introduction Rate (Q) |  |  | 186.486 | cfm
Min. Air Change Required for Adequate Ventilation |  |  | 0.20898 | cfm
*Others includes: instruments, loading arms, pressure relief valves, stuffing boxes, compressor seals, dump lever arms, vents
References
[1] | API RP-505
[2] | API PUBL No. 4615