## Sheet 1
Steps to Calculate Fugitive Emissions Required Ventilation due to Fugitive Emissions
1. Find Building Information and populate all deminsions
2. Set contingency factor based on how confident you feel with current P&ID Rev.
3. Using the P&IDs count and catorgrize all items were fugitives emsiions may leak from
4. Select the appropriate facility type
5. Populate gas stream information.
Formula's Used in Calculations
Corrected Volume [ft3/lb-mol] = V
V = (Vconst x Ta) / Tconst |  |  | Where: | Vconst = 359 [ft3]
Ta = Ambient Building Temperature in Rankine
Tconst = 492 [R]
Total Hydrocarbon leak Rate [cfm] = G
G = [( E) (V)] / [60 x mwavg] |  |  | Where: | E = Emission Rate [lb/hr]
V = Corrected Volume [ft3/lb-mol]
mwavg = Average Molecular Weight
Fresh Air Introduction Rate [cfm] = Qr
Qr = G/C |  |  | Where: | G = Total Hydrocarbon Leak Rate [cfm]
C = LEL x 5% concentration
Minimum Fresh Air Introduction Rate [cfm] = Q
Q = Qr x 4 |  |  | Where: | Qr = Fresh Air Quality Rate [cfm]
4 = Safety Factor (API RP-505 para. )
Minimum Air Change Required Per Hour
= (Q x 60) /Bldg. Vol.
Steps to Calculate the Buildings Natural Ventilation
1. Measure the distance from the center of the lower and upper building vents
2. Determine the number and size of vents on building
3. Determine what case you would like to study to set louver opening percent (i.e. 100% open for summer season)
Formula's Used in Calculations
Neutral Pressure Level [m] = h
h= | H | (Assume Ti > To) | Where: | h = Neutral Pressure Level above center of lower vent [m]
| 1 + [(A1/A2)2(Ti/To)] |  |  | A1 = Free area of lower vent [m2]
A2 = Free area of upper vent [m2]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
H = Vertical distance (center-t-center) between A1 and A2 [m]
Air Flow due to Stack Effect [m3/hr] = Q
Q = [15940 (Cv)(A) [h (Ti - To) / Ti]1/2 ] x 2 |  |  | Where: | 15940 = Conversion Factor
Cv = Effectiveness of Openings (Percent open values)
If A1 and A2 are not equal, Q is multiplyed but corrention |  |  |  | A = Area of the smallest of the lower and upeer vents [m2]
factor from API RP-500 Figure 1. |  |  |  | h = Neutral Pressure Level [m]
Ti = Internal Building Tempature [K]
To = External Building Tempature [K]
2 = Safety Factor (API RP-500 para. 6.3.2.4.5)
Air Changes Per Hour due to Stack Effect
= (Q x 60) /Bldg. Vol.
References
[1] | API RP-505
[2] | API RP-500
[3] | ASHRAE Handbook, Chapter 22